## Instructions
Fan Comparison Spreadsheet
Evaluates total cost of purchasing and operating fans
Change values only in | highlighted cells to compare different: | to compare different:
Interest rates
Loan lengths
Fan models and fan performance
Building sizes
Once several available fans are decided upon, data can be obtained from Bess Labs
at the University of Illinois (www.bess.uiuc.edu)
Once connected, select performance test, current performance tests, 60 HZ, and the
specific fans of interest. Write the data down.
In addition to the manufaturer and model number, you will need horsepower and both
CFM and CFM per Watt, as measured at a static pressure (SP) of 0.10.
Enter this data into the shaded areas for each fan selected.
If you just want to look at operation cost, put the fan purchase price in as $0.00

## 0.10" same size diff HP output
Fan Value Comparison - |  | Same Size Fans with Different Airflows and Efficiencies
| Annual Interest Rate | Length of Loan (yr)
| 8% | 10
Fan Specifications & Performance
| Example Fan #1 | Example Fan #2 | Example Fan #3 | Example Fan #4
Bess Labs Test Number | ----- | ----- | ----- | -----
Manufacturer | ----- | ----- | ----- | -----
Model | ----- | ----- | ----- | -----
Catalog No. | ----- | ----- | ----- | -----
Horse Power | 1 | 1.5 | 1 | 1.5
Size / Drive | 50" / Belt | 50" / Belt | 54" / Belt | 54" / Belt
Shutter | Plastic | Plastic | Aluminum | Aluminum
Housing / Cone | Galvanized | Galvanized | Galvanized | Galvanized
Assumed Grower Cost Each: | 740 | 765 | 965 | 975
Static Pressure Used | 0.1 | 0.1 | 0.1 | 0.1
CFM | 22400 | 25800 | 23500 | 27500
CFM/Watt | 20.1 | 16.4 | 24.5 | 18.1
Building Ventilation Performance
Width (ft) | 40 | 40 | 40 | 40
Length (ft) | 500 | 500 | 500 | 500
Eave height (ft) | 7.5 | 7.5 | 7.5 | 7.5
Peak height (ft) | 10.5 | 10.5 | 10.5 | 10.5
Number Fans Used | 10 | 9 | 10 | 8
Total Building CFM | 224000 | 232200 | 235000 | 220000
Air Exchange (sec) | 48.2143 | 46.5116 | 45.9574 | 49.0909
Tunnel Velocity (FPM) | 622.2222 | 645 | 652.7778 | 611.1111
Yearly Electrical Cost
Power Cost ($/kWh) = | 0.1 | 0.1 | 0.1 | 0.1
Operation (hrs/year) = | 3000 | 3000 | 3000 | 3000
Yearly Power Cost = | 3343.2836 | 4247.561 | 2877.551 | 3646.4088
Fan Purchase Cost
Fan System Cost | 7400 | 6885 | 9650 | 7800
Yearly Payment = | 1102.8182 | 1026.068 | 1438.1346 | 1162.43
Total Purchase and Operation Cost
Total Yearly Cost = | 4446.1018 | 5273.629 | 4315.6856 | 4808.8389
Total Cost Over Loan | 44461.018 | 52736.2901 | 43156.8559 | 48088.3885
Notes:
- Operation Hours Based on 34.25% of 8,760 hour year. (Fans run approx. 1/3 of time)